[image: image1.jpg]goal eodl

ENAPXIAKOE OPFANIEMOE | DISTRICTLOCAL GOVERNMENT
AYTOAIOIKHEHE AAPNAKAT | ORGANIZATION OF LARNAKA





Intention for Procurement Notice
	Title:
	EOAL 63/2025 
Supply, Installation, Commissioning and Maintenance of a Pilot Biomass Pyrolysis System for Wastewater Sludge at Larnaka WWTP

	Contract Scope
	The scope of the contract includes the procurement, transport, installation, commissioning, and a two-year maintenance period for one fully containerized demonstration pyrolysis unit to be deployed at the designated site in Larnaka, Cyprus. Key activities covered under the contract are:
· Transport to site in Larnaka, Cyprus
· Installation and connection to the local power grid
· Commissioning, including functional testing of the unit
· Training of operational personnel to ensure safe and effective operation
· Two-year maintenance period, during which the supplier shall perform all maintenance activities as required by the unit manufacturer, in accordance with the Operation and Maintenance Manual.

The supplier is expected to ensure the unit becomes fully operational and remains in optimal condition throughout the maintenance period.

	Estimated Value
	Three hundred thousand euros (€ 300,000.00) exclusive of VAT as follows:

Supply, installation, and commissioning of one (1) biomass pyrolysis unit corresponding to the amount of two million one hundred fifty thousand Euros (€ 250,000.00)

Two-year maintenance period corresponds to the amount of 50,000 Euros (€ 50,000.00)

	Economic and financial standing
	The average annual turnover for the last three (3) financial years (2024,2023,2022) must be at least equal to Two Hundred Thousand Euros (€200,000.00) Euro. 

	Estimated date of publication of the competition:
	December 2025

	CPV Codes:
	42996000-4
42940000-7
42993000-3
42914000-1
42990000-2
44613800-8
42000000-6
42942000-1

	All qualified and interested suppliers are invited to review the forthcoming tender details and confirm their readiness to participate. Preliminary technical specifications are provided in Annex A. 
Interested parties are encouraged to express their interest and share any comments or opinions with Mr. Pavlos Michael via email at pmichael@eoal.org.cy  or by telephone at 00357 99530976. Feedback should be submitted no later than 21 November 2025, to allow for consideration and potential amendments where applicable.


ANNEX A: Preliminary Technical Specifications

	Type: Biomass Pyrolysis System

	
	Specifications
	Minimum Requirements

	The system consists of:

	1
	Continuous or Batch Operation
	Minimum feed: 75 kg/hour for continuous operation or 350 kg per batch cycle for batch operation.

	2
	Minimum Operating Temperature
	500 oC

	3
	Maximum Operating Temperature
	800 oC

	4
	Reactor Material
	Stainless steel with a minimum resistance to operating temperatures of 1050°C

	5
	Feeding System
	Minimum material quality for components in contact with the processed medium: stainless steel grade EN 1.4301

	6
	Condenser
	Minimum material quality for components in contact with the processed medium: stainless steel grade EN 1.4301

	7
	Syngas Cleaning System
	Minimum material quality for components in contact with the processed medium: stainless steel grade EN 1.4301

	8
	Extraction System
	Minimum material quality for components in contact with the processed medium: stainless steel grade EN 1.4301

	9
	Gas Pipes
	Minimum material quality for components in contact with the processed medium: stainless steel grade EN 1.4301

	10
	Ability to measure produced syngas gas
	Syngas sampling and cooling for humidity/oil condensation; flow and gas composition (CO, CO2, N2, CH4, H2) sensors.

	11
	Control
	Electronic control via PLC of:

· Motors

· Pumps

· Ventilation

· Burner

	12
	Monitoring
	· Temperatures

· Pressures

	13
	Operation and Monitoring
	Remote Control

	14
	Self-sufficient Installation
	The main structure and equipment must be installed on a standard 20- or 40-foot container.

	15
	Total Required Area
	The fully developed unit must be deployable within an area measuring 15 by 10 meters, and the maximum height of any component should not exceed 4.0 meters.

	16
	Input moisture
	Up to 30%

	17
	Retention time
	In the case of continuous reactor, the possibility to modify the retention time up to 1 hour

	18
	Burner
	Produced syngas must be burnt in a burner able to accept both syngas and liquid propane gas/natural gas for start-up.

Measure of the exhaust gases flow rate.

	19
	Emissions
	Exhaust gases from the burner must comply with:

Table 1 – Emission limits assumed for the syngas burner emissions.

Dust

20 mg/Nm3
Nitrous oxides (as NO2)

200 mg/Nm3
Sulphur oxide (SO2)

100 mg/Nm3
Carbon monoxide (CO)

150 mg/Nm3
Total Organic Carbon (TOC)

20 mg/Nm3
Ammonia (NH3) [*]

5 mg/Nm3
[*] It applies in the case where abatement systems using urea or ammonia are adopted for nitrogen oxides removal.

	20
	Operating pressure
	The pressure inside the reactor must be kept 10-20 mb higher than the ambient pressure

	21
	Feeding and extraction systems
	Must be able not to let any air into the reactor

	22
	Noise
	< 80 dB


Page 1 of 2

[image: image1.jpg]